## Sites
[46 empty] | Water Resources RAG descriptions |  | Water Supply RAG descriptions | [11 empty] | WwTW Flow Capacity RAG descriptions |  |  |  | Foul Sewerage RAG descriptions | [6 empty] | Odour Screening RAG descriptions |  | Effluent flood risk RAG descriptions |  | Water Quality RAG descriptions |  | WwTW Flow Capacity RAG descriptions |  | WwTW Flow Capacity RAG descriptions
[46 empty] | Adopted WRMP has planned for the increase in demand, or sufficient time to address supply demand issues in the next WRMP. |  | Capacity available to serve the proposed growth | [11 empty] | Capacity available to serve the proposed growth |  |  |  | Capacity available to serve the proposed growth |  | Capacity available to serve the proposed growth |  |  |  |  | Site is unlikely to be impacted by odour from WwTW |  | Additional flow ≤5% of Q30. Low risk that increased discharges will increase fluvial flood risk. |  | Sufficient Environmental Capacity. Proposed development has no significant impact on the water body's potential for reaching GES. |  |  |  | Capacity available to serve the proposed growth
[25 empty] | 2177 | [20 empty] | Insufficient evidence in adopted WRMP to confirm that the planned increase in demand can be met |  | Infrastructure and/or treatment work upgrades are required to serve proposed growth, but no significant constraints to the provision of this infrastructure have been identified . | [11 empty] | Infrastructure and/or treatment work upgrades are required to serve proposed growth, but no significant constraints to the provision of this infrastructure have been identified . |  |  |  | Infrastructure and/or treatment work upgrades are required to serve proposed growth, but no significant constraints to the provision of this infrastructure have been identified . |  | Infrastructure and/or treatment work upgrades are required to serve proposed growth, but no significant constraints to the provision of this infrastructure have been identified . |  |  |  |  | Site location is such that an odour impact assessment is recommended |  | Additional flow ≥5% of Q30. Moderate risk that increased discharges will increase fluvial flood risk. |  | Proposed development can be accommodated with a tighter permit and upgrade to treatment. This is achievable with current technology. |  |  |  | Infrastructure and/or treatment work upgrades are required to serve proposed growth, but no significant constraints to the provision of this infrastructure have been identified .
[46 empty] | Adopted WRMP does not take into consideration the planned increase in demand. Additional water resources may be required. |  | Infrastructure and/or treatment upgrades will be required to serve proposed growth. Major constraints have been identified. | [11 empty] | Infrastructure and/or treatment upgrades will be required to serve proposed growth. Major constraints have been identified. |  |  |  | Infrastructure and/or treatment upgrades will be required to serve proposed growth. Major constraints have been identified. |  | Infrastructure and/or treatment upgrades will be required to serve proposed growth. Major constraints have been identified. |  |  |  |  | Site is in an area with confirmed WwTW odour issues. |  | Additional flow ≥5% of Q100. High risk that increased discharges will increase fluvial flood risk. |  | Good Ecological Status cannot be achieved due to current technology limits. Ensure proposed growth doesn't cause significant deterioration. |  |  |  | Infrastructure and/or treatment upgrades will be required to serve proposed growth. Major constraints have been identified.
Environmental capacity could be a constraint to growth
Site information | [15 empty] | Trajectory: "Residential" = number of dwellings, "Employment"=number of employees, "Mixed" = percentage of development | [19 empty] | Water Supply | [13 empty] | Wastewater
Policy No. / PP Application No. | Trajectory Ref | GIS ID | Local Planning Authority | In study area? | Type | Parish / Settlement | Location | Status | Site Area (Ha) | Current Use | Proposed Use | Potential housing number (2015-35) | Potential employment space (m2) (2015-2035) | Employment land class | Number of employees | Completed 2015-Dec 2017 | 17/18 | 18/19 | 19/20 | 20/21 | 21/22 | 22/23 | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | 30/31 | 31/32 | 32/33 | 33/34 | 34/35 | Check | Water Company | Water Resource Zone | Per capita domestic consumption (m3/p/d) | Average occupancy (persons per household) | Per capita employment consumption (m3/p/d) | Demand (Ml/d) | Demand by end of AMP6 (Ml/d) | Demand by end of AMP7 (Ml/d) | Demand by end of AMP8 (Ml/d) | Demand by end of AMP9 (Ml/d) | Water Resources RAG | Water Resources Comments | Water Supply Networks RAG | Water Supply Networks Comments | Company Treating Wastewater | WwTW | Percentage of water used returned to sewer | Wastewater Demand (Ml/d) | Wastewater Demand by end of AMP6 (Ml/d) | Wastewater Demand by end of AMP7 (Ml/d) | Wastewater Demand by end of AMP8 (Ml/d) | Wastewater Demand by end of AMP9 (Ml/d) | Average Foul Flow (m3/s) | Sewers for Adoption Design Foul Flow (m3/s) | WwTW Flow Capacity RAG - Thames Water Assessment | WwTW Flow Capacity - Thames Water Comments | Sewerage Undertaker | Sewerage catchment | Foul Sewerage Network Capacity RAG - Thames Water Assessment | Foul Sewerage Network Capacity - Thames Water Comments | Overall wastewater RAG | Overall wastewater comments | Site boundary distance from WwTW (m) | Site encroaches closer than existing urban area? | Location of site relative to WwTW | Odour Screening RAG - JBA Assessment | Odour screening - Thames Water Comments | Effluent discharge flood risk RAG - JBA Assessment | Effluent discharge flood risk - Thames Water Comments | Water Quality RAG - JBA Assessment | Water Quality - JBA Comments | Overall wastewater RAG | Overall wastewater comments | Surface Water Network capacity - Thames Water Assessment | Surface Water Network Capacity - Thames Water Comments | Implications for Surface Water Connections from New Development - JBA Comments | Feasibility of Discharging Surface Water from the Site (based on topography and presence of water bodies) - JBA Comments
HS2-1 |  | HS2-1 | Harlow District Council | Yes | Housing | Harlow | Princess Alexandra Hospital | Emerging allocation | 14.0057 | Employment | Residential | 650 |  |  | #N/A |  | 28/29: 200; 29/30: 200; 30/31: 200; 31/32: 50 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.21649 | 0 | 0 | 0.13322 | 0.21649 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.20566 | 0 | 0 | 0.12656 | 0.20566 | 0.0023804 | 0.039897 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Amber | TW Comments (09/08/2018): 'Detailed modelling is still in progress for these sites but all RAG classifications remain the same'. |  |  | 4150 | No | East to Rye Meads | Green | TW comment (04/04/2018): don’t expect issues | Green |  | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint. There may be opportunities to discharge surface water into the pond at the south east of the site. The use of rainfwater harvesting should be investigated.
HS2-2 |  | HS2-2 | Harlow District Council | Yes | Housing | Harlow | The Stow Service Bays | Emerging allocation | 0.50478 | Residential | Residential | 70 |  |  | #N/A |  | 19/20: 70 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.023314 | 0.023314 | 0.023314 | 0.023314 | 0.023314 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.022148 | 0.022148 | 0.022148 | 0.022148 | 0.022148 | 0.00025635 | 0.0035941 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Amber |  |  |  | 6230/5940 | No | East to Rye Meads/North to Thornwood | Green | TW comment (04/04/2018): don’t expect issues | Green |  | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint, as the site is not located close to a water body. The use of rainfwater harvesting should be investigated.
HS2-3 |  | HS2-3 | Harlow District Council | Yes | Housing | Harlow | Land east of Katherines Way, west of Deer Park | Emerging allocation | 2.3603 | Greenfield | Residential | 69 |  |  | #N/A |  | 28/29: 69 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.022981 | 0 | 0 | 0.022981 | 0.022981 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.021832 | 0 | 0 | 0.021832 | 0.021832 | 0.00025269 | 0.0048467 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Green | TW Comments (09/08/2018): 'Detailed modelling is still in progress for these sites but all RAG classifications remain the same'. |  |  | 4145 | No | East to Rye Meads | Green | TW comment (04/04/2018): don’t expect issues | Green |  | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint, however the site slopes northeastwards towards Parndon Brook, which is located 50m to the east. Large open green spaces lie to the north and east of the site, and may provide opportuniteis for managing surface water.
HS2-4 |  | HS2-4 | Harlow District Council | Yes | Housing | Harlow | Lister House, Staple Tye Mews, Staple Tye Depot and The Gateway Nursery | Emerging allocation | 0.96217 | Residential | Residential | 42 |  |  | #N/A |  | 20/21: 20; 21/22: 22 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.013989 | 0.0066612 | 0.013989 | 0.013989 | 0.013989 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.013289 | 0.0063281 | 0.013289 | 0.013289 | 0.013289 | 0.00015381 | 0.002618 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Amber |  |  |  | 5138/4392 | No | East to Rye Meads/North -West to Thornwood | Green | TW comment (04/04/2018): don’t expect issues | Green |  | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint, as the site is not located close to a water body. Open green spaces lie to the east and north of the site, and may provide opportunities for amanaging surface water. The use of rainfwater harvesting should be investigated.
HS2-5 |  | HS2-5 | Harlow District Council | Yes | Housing | Harlow | South of Clifton Hatch | Emerging allocation | 0.77159 | Greenfield | Residential | 36 |  |  | #N/A |  | 27/28: 36 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.01199 | 0 | 0 | 0.01199 | 0.01199 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.011391 | 0 | 0 | 0.011391 | 0.011391 | 0.00013184 | 0.0022068 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Green | TW Comments (09/08/2018): 'Detailed modelling is still in progress for these sites but all RAG classifications remain the same'. |  |  | 6963/3224 | No | East - South to Rye Meads/North -West to Thornwood | Green | TW comment (04/04/2018): don’t expect issues | Green |  | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Red | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint, as the site is not located close to a water body. The use of rainfwater harvesting should be investigated.
HS2-6 |  | HS2-6 | Harlow District Council | Yes | Housing | Harlow | Riddings Lane | Emerging allocation | 1.5463 | Greenfield | Residential | 35 |  |  | #N/A |  | 23/24: 35 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.011657 | 0 | 0.011657 | 0.011657 | 0.011657 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.011074 | 0 | 0.011074 | 0.011074 | 0.011074 | 0.00012817 | 0.0027027 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Amber |  |  |  | 6801/2960 | No | East - South to Rye Meads/North -West to Thornwood | Green | TW comment (04/04/2018): don’t expect issues | Green |  | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Red | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The site could drain north westwards into the watercourse forming the western border of the site.
HS2-7 |  | HS2-7 | Harlow District Council | Yes | Housing | Harlow | Kingsmoor Recreation Centre | Emerging allocation | 0.81819 | Greenfield | Residential | 35 |  |  | #N/A |  | 24/25: 35 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.011657 | 0 | 0.011657 | 0.011657 | 0.011657 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.011074 | 0 | 0.011074 | 0.011074 | 0.011074 | 0.00012817 | 0.0021931 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Amber |  |  |  | 4790/4607 | No | East - South to Rye Meads/North -West to Thornwood | Green | TW comment (04/04/2018): don’t expect issues | Green |  | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint, as the site is not located close to a water body. Two small open green areas lie downstream of the site, and may provide opportunities for managing the rate and volume of surface water runoff leaving the site. The use of rainfwater harvesting should be investigated.
HS2-8 |  | HS2-8 | Harlow District Council | Yes | Housing | Harlow | The Evangelical Lutheran Church, Tawneys Road | Emerging allocation | 0.17599 | Unknown | Residential | 35 |  |  | #N/A |  | 21/22: 35 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.011657 | 0 | 0.011657 | 0.011657 | 0.011657 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.011074 | 0 | 0.011074 | 0.011074 | 0.011074 | 0.00012817 | 0.0017436 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Amber |  |  |  | 6383/4045 | No | East - South to Rye Meads/North -West to Thornwood | Green | TW comment (04/04/2018): don’t expect issues | Green |  | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Red | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint, as the site is not located close to a water body. The use of rainfwater harvesting should be investigated.
HS2-9 |  | HS2-9 | Harlow District Council | Yes | Housing | Harlow | Land east of 144-154 Fennells | Emerging allocation | 0.81528 | Greenfield | Residential | 23 |  |  | #N/A |  | 30/31: 23 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0076604 | 0 | 0 | 0 | 0.0076604 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0072774 | 0 | 0 | 0 | 0.0072774 | 8.4229e-05 | 0.0016355 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Green | TW Comments (09/08/2018): 'Modelling has only been completed until 2026. We are arranging for this to be extended to cover the plan period' |  |  | 5458/3972 | No | East - South to Rye Meads/North -West to Thornwood | Green | TW comment (04/04/2018): don’t expect issues | Green |  | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint, as the closest watercourse lies upslope of the site. The use of rainfwater harvesting should be investigated.
HS2-10 |  | HS2-10 | Harlow District Council | Yes | Housing | Harlow | Pollard Hatch plus garages and adjacent land | Emerging allocation | 0.33389 | Residential | Residential | 20 |  |  | #N/A |  | 21/22: 20 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0066612 | 0 | 0.0066612 | 0.0066612 | 0.0066612 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0063281 | 0 | 0.0063281 | 0.0063281 | 0.0063281 | 7.3242e-05 | 0.0011596 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Green |  |  |  | 4351 | No | East to Rye Meads | Green | TW comment (04/04/2018): don’t expect issues | Green |  | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint. The site slopes north-westwards towards Parndon Brook, which lies approx. 250m away. The use of rainfwater harvesting should be investigated.
HS2-11 |  | HS2-11 | Harlow District Council | Yes | Housing | Harlow | Land between Second Avenue and St. Andrews Meadow | Emerging allocation | 0.40988 | Greenfield | Residential | 16 |  |  | #N/A |  | 20/21: 16 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.005329 | 0.005329 | 0.005329 | 0.005329 | 0.005329 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0050625 | 0.0050625 | 0.0050625 | 0.0050625 | 0.0050625 | 5.8594e-05 | 0.0010277 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Green |  |  |  | 6174/4774 | No | East to Rye Meads/North -West to Thornwood | Green | TW comment (04/04/2018): don’t expect issues | Green |  | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Red | TW comment (04/04/2018): Discharge unknown but sites located in known very limited sewer capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint. The site slopes towards the Todd Brook and Nettleswell Pond, which lie approx. 150m north east of the site. The use of rainfwater harvesting should be investigated.
HS2-12 |  | HS2-12 | Harlow District Council | Yes | Housing | Harlow | Coppice Hatch and garages | Emerging allocation | 0.33535 | Residential | Residential | 16 |  |  | #N/A |  | 29/30: 16 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.005329 | 0 | 0 | 0.005329 | 0.005329 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0050625 | 0 | 0 | 0.0050625 | 0.0050625 | 5.8594e-05 | 0.00097549 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Green | TW Comments (09/08/2018): 'Modelling has only been completed until 2026. We are arranging for this to be extended to cover the plan period' |  |  | 5342/4635 | No | East to Rye Meads/North -West to Thornwood | Green | TW comment (04/04/2018): don’t expect issues | Green |  | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint, as the site is not located close to a water body. The site slopes towards an unnamed tributary of the Todd Brook which lies approx. 200m east of the site. The use of rainfwater harvesting should be investigated.
HS2-13 |  | HS2-13 | Harlow District Council | Yes | Housing | Harlow | Sherards House | Emerging allocation | 0.48028 | Residential | Residential | 15 |  |  | #N/A |  | 24/25: 15 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0049959 | 0 | 0.0049959 | 0.0049959 | 0.0049959 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0047461 | 0 | 0.0047461 | 0.0047461 | 0.0047461 | 5.4932e-05 | 0.0010306 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Green |  |  |  | 4330 | No | East to Rye Meads | Green | TW comment (04/04/2018): don’t expect issues | Green |  | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint, as the site is not located close to a water body. A large open green space is located downslope of the site and may provide opportunities for managing surface water. The use of rainfwater harvesting should be investigated.
HS2-14 |  | HS2-14 | Harlow District Council | Yes | Housing | Harlow | Elm Hatch and public house | Emerging allocation | 0.20064 | Mixed | Residential | 13 |  |  | #N/A |  | 19/20: 13 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0043298 | 0.0043298 | 0.0043298 | 0.0043298 | 0.0043298 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0041133 | 0.0041133 | 0.0041133 | 0.0041133 | 0.0041133 | 4.7608e-05 | 0.0007423 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Green |  |  |  | 6027/4738 | No | East to Rye Meads/North -West to Thornwood | Green | TW comment (04/04/2018): don’t expect issues | Green |  | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Red | TW comment (04/04/2018): Discharge unknown but sites located in known very limited sewer capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint, as the site is not located close to a water body. The site slopes towards the Todd Brook and Nettleswell Pond, which lie approx. 160m north of the site, and may provide an opportunity for discharge. The use of rainfwater harvesting should be investigated.
HS2-15 |  | HS2-15 | Harlow District Council | Yes | Housing | Harlow | Playground west of 93 – 100 Jocelyns | Emerging allocation | 0.39335 | Greenfield | Residential | 12 |  |  | #N/A |  | 30/31: 12 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0039967 | 0 | 0 | 0 | 0.0039967 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0037969 | 0 | 0 | 0 | 0.0037969 | 4.3945e-05 | 0.0008309 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Green | TW Comments (09/08/2018): 'Modelling has only been completed until 2026. We are arranging for this to be extended to cover the plan period' |  |  | 7498/5905 | No | East to Rye Meads/West - South to Hatfield Heath | Green | TW comment (04/04/2018): don’t expect issues | Green | TW comment (04/04/2018): not known issues | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in know limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint, as the site is not located close to a water body. The use of rainfwater harvesting should be investigated.
HS2-16 |  | HS2-16 | Harlow District Council | Yes | Housing | Harlow | Fishers Hatch | Emerging allocation | 0.19182 | Residential | Residential | 10 |  |  | #N/A |  | 29/30: 10 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0033306 | 0 | 0 | 0.0033306 | 0.0033306 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0031641 | 0 | 0 | 0.0031641 | 0.0031641 | 3.6621e-05 | 0.00059723 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Green | TW Comments (09/08/2018): 'Modelling has only been completed until 2026. We are arranging for this to be extended to cover the plan period' |  |  | 5705 | No | East to Rye Meads | Green | TW comment (04/04/2018): don’t expect issues | Green | TW comment (04/04/2018): not known issues | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint, as the site is not located close to a water body. The use of rainfwater harvesting should be investigated.
HS2-17 |  | HS2-17 | Harlow District Council | Yes | Housing | Harlow | Slacksbury Hatch and associated garages | Emerging allocation | 0.23642 | Residential | Residential | 10 |  |  | #N/A |  | 19/20: 10 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0033306 | 0.0033306 | 0.0033306 | 0.0033306 | 0.0033306 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0031641 | 0.0031641 | 0.0031641 | 0.0031641 | 0.0031641 | 3.6621e-05 | 0.00062846 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Green |  |  |  | 4273 | No | East to Rye Meads | Green | TW comment (04/04/2018): don’t expect issues | Green | TW comment (04/04/2018): not known issues | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint, as the site is not located close to a water body. The use of rainfwater harvesting should be investigated.
HS2-18 |  | HS2-18 | Harlow District Council | Yes | Housing | Harlow | Garage blocks adjacent to Nicholls Tower | Emerging allocation | 0.34176 | Residential | Residential | 10 |  |  | #N/A |  | 31/32: 10 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0033306 | 0 | 0 | 0 | 0.0033306 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0031641 | 0 | 0 | 0 | 0.0031641 | 3.6621e-05 | 0.00070219 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Green | TW Comments (09/08/2018): 'Modelling has only been completed until 2026. We are arranging for this to be extended to cover the plan period' |  |  | 6866/4504 | No | East to Rye Meads/North -West to Thornwood | Green | TW comment (04/04/2018): don’t expect issues | Green | TW comment (04/04/2018): not known issues | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Red | TW comment (04/04/2018): Discharge unknown but sites located in known very limited sewer capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint. A tributary of the Todd Brook may lie north of the site, but would require a long section of culvert to connect. The site slopes northwards towards a large area of open green space, which may contain an provide opportunities for managing surface water. The use of rainfwater harvesting should be investigated.
HS2-19 |  | HS2-19 | Harlow District Council | Yes | Housing | Harlow | Stewards Farm | Emerging allocation | 0.49561 | Residential | Residential | 10 |  |  | #N/A |  | 28/29: 10 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0033306 | 0 | 0 | 0.0033306 | 0.0033306 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0031641 | 0 | 0 | 0.0031641 | 0.0031641 | 3.6621e-05 | 0.00080989 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Green | TW Comments (09/08/2018): 'Modelling has only been completed until 2026. We are arranging for this to be extended to cover the plan period' |  |  | 6079/3549 | No | East - South to Rye Meads/North -West to Thornwood | Green | TW comment (04/04/2018): don’t expect issues | Green | TW comment (04/04/2018): not known issues | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Red | TW comment (04/04/2018): Discharge unknown but sites located in known very limited sewer capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint. The site is not located close to a surface water body. A small open green space is located downslope of the site, and may provide opportunities for managing surface water. The use of rainfwater harvesting should be investigated.
HS2-20 |  | HS2-20 | Harlow District Council | Yes | Housing | Harlow | Land between Barn Mead and Five Acres | Emerging allocation | 0.32094 | Greenfield | Residential | 10 |  |  | #N/A |  | 29/30: 10 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0033306 | 0 | 0 | 0.0033306 | 0.0033306 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0031641 | 0 | 0 | 0.0031641 | 0.0031641 | 3.6621e-05 | 0.00068762 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Green | TW Comments (09/08/2018): 'Modelling has only been completed until 2026. We are arranging for this to be extended to cover the plan period' |  |  | 5720/4188 | No | East to Rye Meads/North -West to Thornwood | Green | TW comment (04/04/2018): don’t expect issues | Green | TW comment (04/04/2018): not known issues | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint. The site is not located close to a surface water body. An open green space lies 70m east of the site, and may provide opportunities for managing surface water. The use of rainfwater harvesting should be investigated.
HS2-21 |  | HS2-21 | Harlow District Council | Yes | Housing | Harlow | Pypers Hatch | Emerging allocation | 0.20159 | Residential | Residential | 10 |  |  | #N/A |  | 31/32: 10 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0033306 | 0 | 0 | 0 | 0.0033306 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0031641 | 0 | 0 | 0 | 0.0031641 | 3.6621e-05 | 0.00060408 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Green | TW Comments (09/08/2018): 'Modelling has only been completed until 2026. We are arranging for this to be extended to cover the plan period' |  |  | 6188 | No | East to Rye Meads | Green | TW comment (04/04/2018): don’t expect issues | Green | TW comment (04/04/2018): not known issues | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint, as the site is not located close to a water body. The site is located upslope of a small open green space, which may provide opportunities for managing surface water. The use of rainfwater harvesting should be investigated.
HS3 |  | HS3 | Harlow District Council | Yes | Housing | Harlow | Strategic Housing Site East of Harlow | Emerging allocation | 109.103 | Greenfield | Residential | 2600 |  |  | #N/A |  | 20/21: 100; 21/22: 200; 22/23: 250; 23/24: 300; 24/25: 300; 25/26: 300; 26/27: 300; 27/28: 300; 28/29: 300; 29/30: 250 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.86596 | 0.033306 | 0.38302 | 0.86596 | 0.86596 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.82266 | 0.031641 | 0.36387 | 0.82266 | 0.82266 | 0.0095215 | 0.19674 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Amber | TW Comments (09/08/2018): 'Modelling has only been completed until 2026. We are arranging for this to be extended to cover the plan period' |  |  | 8680/3699 | No | East to Rye Meads/West - South to Hatfield Heath | Green | TW comment (04/04/2018): don’t expect issues | Green | TW comment (04/04/2018): not known issues | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in know limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | Harlowbury Brook borders both the upper and lower site. The upper site could drain south-westwards into the watercourse, whereas the lower site could drain northwards into the brook.
ED1-01 |  | ED1-01 | Harlow District Council | Yes | Employment | Harlow | Harlow Business Park, The Pinnacles | Emerging allocation | 4.7016 | Greenfield | Employment | 0 | 23000 | B1a | 2875 |  |  |  |  | 262 | 262 | 262 | 262 | 261 | 261 | 261 | 261 | 261 | 261 | 261 |  |  |  |  | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.2875 | 0.0262 | 0.1309 | 0.2614 | 0.2875 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.27312 | 0.02489 | 0.12436 | 0.24833 | 0.27312 | 0.0031612 | 0.0032911 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Amber | TW Comments (09/08/2018): 'Detailed modelling is still in progress for these sites but all RAG classifications remain the same'. |  |  | 2588 | No | East to Rye Meads | Green | TW comment (04/04/2018): don’t expect issues | Green | TW comment (04/04/2018): not known issues | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | An unnamed ordinary watercourse lies approx. 40m north of the site. The site could drain northwards into this watercourse, however a connecting section of culvert would be required beneath Roydon Road. Open green spaces lie to the east and north of the site, and may provide opportunities for managing the rate and volume of surface water runoff leaving the site.
ED1-02 |  | ED1-02 | Harlow District Council | Yes | Employment | Harlow | London Road | Emerging allocation | 15.7124 | Greenfield | Employment | 0 | 71000 | B1a | 8875 |  |  |  |  | 807 | 807 | 807 | 807 | 807 | 807 | 807 | 807 | 807 | 807 | 805 |  |  |  |  | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.8875 | 0.0807 | 0.4035 | 0.807 | 0.8875 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.84312 | 0.076665 | 0.38333 | 0.76665 | 0.84312 | 0.0097584 | 0.010999 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Amber | TW Comments (09/08/2018): 'Detailed modelling is still in progress for these sites but all RAG classifications remain the same'. |  |  | 7288/5972 | No | East to Rye Meads/West - South to Hatfield Heath | Green | TW comment (04/04/2018): don’t expect issues | Green | TW comment (04/04/2018): not known issues | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint. The site is not located close to a water body. The site is located upslope of a large open green space (school playing field), which may provide opportunities for the management of surface water. The use of rainfwater harvesting should be investigated.
ED1-03 |  | ED1-03 | Harlow District Council | Yes | Employment | Harlow | East Road, Templefields | Emerging allocation | 2.2272 | Greenfield | Employment | 0 | 11000 | B1a | 1375 |  |  |  |  | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 |  |  |  |  | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.1375 | 0.0125 | 0.0625 | 0.125 | 0.1375 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.13062 | 0.011875 | 0.059375 | 0.11875 | 0.13062 | 0.0015119 | 0.001559 | Green | TW Comment (31/07/2018): 'Our assessment confirms that we will have capacity at the treatment works up until 2036 and do not have any concerns related to the sites consulted'. | Thames Water Utilities Limited | Rye Meads | Amber | TW Comments (09/08/2018): 'Detailed modelling is still in progress for these sites but all RAG classifications remain the same'. |  |  | 7177/5930 | No | East to Rye Meads/West - South to Hatfield Heath | Green | TW comment (04/04/2018): don’t expect issues | Green | TW comment (04/04/2018): not known issues | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | The ability to discharge of surface water is a constraint, as the site is not located close to a water body or any open green spaces. The use of rainfwater harvesting should be investigated.
GA1 |  | GA1 | East Hertfordshire District Council | Yes | Mixed | Harlow-Gilston Garden Town | Gilston Allocation | Allocated | 635.878 | Greenfield | Mixed | 3050 | 25000 | B1a | 3125 | [6 empty] | 7% | 7% | 7% | 5% | 5% | 5% | 5% | 5% | 11% | 11% | 11% | 11% | 10% | -1.1102e-16 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 1.3283 | 0 | 0.27895 | 0.61103 | 1.3283 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 1.2619 | 0 | 0.265 | 0.58048 | 1.2619 | 0.014606 | 0.58632 | Green | TW Comment (31/07/2018):'We do not have a detailed assessment past 2036, but do not foresee future issues with space or water quality for Rye Meads STW'. | Thames Water Utilities Limited | Rye Meads | Green | TW Comments (09/08/2018): 'Modelling has only been completed until 2026. We are arranging for this to be extended to cover the plan period'. 'We currently have confidence in circa 3000 homes on the Gilston site'. |  |  | 2210/1158 | Yes (but only from this site) | North-East to Rye Meads/South to Widford | Green | TW comment (04/04/2018): don’t expect issues | Green | TW comment (04/04/2018): not known issues | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Green | TW comment (04/04/2018): Site not connected to public sewer | No public sewer available to connect into. Option of connecting into private surface water sewer not recommended. | There are several opportuinties for discharge of the site to watercourse, as the Hunsdon Brook, Fiddler's Brook, Golden Brook and an unnamed tributary of the River Stort border the site. The lower site could drain southwards and south-eastwards into any of the watercourses. The upper site could drain southwards, and eastwards into Golden Brook.
RUR.R1 |  | RUR.R1 | Epping Forest District Council | Yes | Housing | Harlow-Gilston Garden Town | Avenue Home, Latton Common, Near Harlow, CM17 9NJ | Emerging allocation | 0.38136 | Greenfield | Residential | 11 |  |  | #N/A |  | 21/22: 11 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0036637 | 0 | 0.0036637 | 0.0036637 | 0.0036637 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0034805 | 0 | 0.0034805 | 0.0034805 | 0.0034805 | 4.0283e-05 | 0.00077621 | Green | TW Comment (31/07/2018):'We do not have a detailed assessment past 2036, but do not foresee future issues with space or water quality for Rye Meads STW'. | Thames Water Utilities Limited | Rye Meads | Green |  |  |  | 7941/3180 | No | East to Rye Meads/West - North to Thornwood | Green | TW comment (04/04/2018): don’t expect issues | Green | TW comment (04/04/2018): not known issues | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | An unnamed ordinary watercourse lies approx. 50m north of the site. The site could drain northwards into this watercourse, however a connecting section of culvert would be required beneath Latton Street.
SP 5.3 |  | SP 5.3 | Epping Forest District Council | Yes | Housing | Harlow-Gilston Garden Town | East of Harlow - Land East of Harlow, North of Church Langley and South of Sheering Road, Harlow, Essex, CM17 0NG | Emerging allocation | 102.3675 | Greenfield | Residential | 750 |  |  | #N/A |  | 22/23: 83; 23/24: 83; 24/25: 84; 25/26: 100; 26/27: 100; 27/28: 100; 28/29: 100; 29/30: 100 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.24979 | 0 | 0.083265 | 0.24979 | 0.24979 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.23731 | 0 | 0.079102 | 0.23731 | 0.23731 | 0.0027466 | 0.10638 | Green | TW Comment (31/07/2018):'We do not have a detailed assessment past 2036, but do not foresee future issues with space or water quality for Rye Meads STW'. | Thames Water Utilities Limited | Rye Meads | Amber | TW Comments (09/08/2018): 'Modelling has only been completed until 2026. We are arranging for this to be extended to cover the plan period' |  |  | 9240/2149 | No | East to Rye Meads/West - South to Hatfield Heath | Green | TW comment (04/04/2018): don’t expect issues | Green | TW comment (04/04/2018): not known issues | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Amber | TW comment (04/04/2018): Discharge unknown but sites located in known limited capacity area | Connection of new development into SW sewer unlikely to be permitted. | Potenital to discharge into the Pincey Brook, which flows through the centre of the site. Northern portion of the site could drain southwards into the watercourses, and the Southern portion could drain northwestwards into the watercourse.
SP 5.1 |  | SP 5.1 | Epping Forest District Council | Yes | Mixed | Harlow-Gilston Garden Town | Latton Priory - Land to east of Rye Hill Road, London Road, Harlow, Essex, CM18 7HT | Emerging allocation | 117.0406 | Greenfield | Mixed | 1050 | 5000 | B1a | 625 | [5 empty] | 4.8% | 9.5% | 9.4% | 9.4% | 9.4% | 9.4% | 9.4% | 9.4% | 9.4% | 9.4% | 10.5% |  |  |  | -1.1102e-16 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.41221 | 0 | 0.13644 | 0.33018 | 0.41221 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.3916 | 0 | 0.12962 | 0.31367 | 0.3916 | 0.0045324 | 0.13054 | Green | TW Comment (31/07/2018):'We do not have a detailed assessment past 2036, but do not foresee future issues with space or water quality for Rye Meads STW'. | Thames Water Utilities Limited | Rye Meads | Red | TW comments (04/04/2018): There is lack of capacity in local sewers and solution has to be implemented on very early stage. |  |  | 6240/2087 | No | South -East to Rye Meads/North -West to Thornwood | Green | TW comment (04/04/2018): don’t expect issues | Green | TW comment (04/04/2018): not known issues | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Red | TW comment (04/04/2018): Discharge unknown but sites located in known very limited sewer capacity area | Connection of new development into SW sewer unlikely to be permitted. | Unnamed ordinary watercourses lies beyond the northern and southern boundaries of the site. Southern portion of the site could drain southwards into the watercourse on Rye Hill Common. Northern portion could drain northwards into the watercourse west of Riddings Lane.
SP 5.2 |  | SP 5.2 | Epping Forest District Council | Yes | Housing | Harlow-Gilston Garden Town | West of Harlow - Water Lane Area | Emerging allocation | 128.2432 | Greenfield | Residential | 2100 |  |  | #N/A | [5 empty] | 100 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 100 | 100 | 100 | 100 |  | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.69943 | 0 | 0.23314 | 0.5662 | 0.69943 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.66445 | 0 | 0.22148 | 0.53789 | 0.66445 | 0.0076904 | 0.18699 | Green | TW Comment (31/07/2018):'We do not have a detailed assessment past 2036, but do not foresee future issues with space or water quality for Rye Meads STW'. | Thames Water Utilities Limited | Rye Meads | Amber | TW Comments (09/08/2018): 'Modelling has only been completed until 2026. We are arranging for this to be extended to cover the plan period' |  |  | 2751 | No | East -South to Rye Meads | Green | TW comment (04/04/2018): don’t expect issues | Green | TW comment (04/04/2018): not known issues | Amber | Predicted impacts of study area growth at Rye Meads WwTW: - 11% deterioration in Ammonia at Rye Meads WwTW (cannot be completely prevented). - Good ecological status cannot be acheved for Phosphate due to current technology limits. - BOD and Phosphate are predicted to deteriorate by <10%. |  |  | Red | TW comment (04/04/2018): Discharge unknown but sites located in known very limited sewer capacity area | Connection of new development into SW sewer unlikely to be permitted. | The Parndon Brook is crosses the southern portion of the upper site. The northern portion of this site could drain southwards into the brook and the smaller southern portion could drain northwestwards into the watercourse. An unnamed ordinary watercourse bordes the lower site. Depending on its capacity, the site could drain north-westwards into this receiving watercourse.
Hospital Relocation A |  | Hospital Relocation A | East Hertfordshire District Council | Yes |  | Harlow-Gilston Garden Town | Gilston (part of) | Emerging | 14 | Greenfield | Unknown | 0 |  |  | #N/A | [19 empty] | FALSE | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0 | Manual calc required | Manual calc required | Manual calc required | Manual calc required |  |  |  |  | Thames Water Utilities Limited | Rye Meads | [10 empty] | Thames Water Utilities Limited | Rye Meads
Hospital Relocation B |  | Hospital Relocation B | Epping Forest District Council | Yes |  | Harlow-Gilston Garden Town | East of Harlow (part of) | Emerging | 14 | Greenfield | Unknown | 0 |  |  | #N/A | [19 empty] | FALSE | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0 | Manual calc required | Manual calc required | Manual calc required | Manual calc required |  |  |  |  | Thames Water Utilities Limited | Rye Meads | [10 empty] | Thames Water Utilities Limited | Rye Meads
04/00302 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Newhall Phase 2 & 3 (750 + 1550 includes 300 Hubbards Hall Land) | Planning permission granted |  |  | Residential | 2177 |  |  | #N/A | 205 | 162 | 71 | 34 | 55 | 108 | 171 | 183 | 302 | 280 | 162 | 122 | 88 | 58 | 48 | 48 | 48 | 32 |  | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.72507 | 0.17552 | 0.42998 | 0.66645 | 0.72507 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.68882 | 0.16675 | 0.40848 | 0.63313 | 0.68882 | 0.0079724 | 0.10079 |  |  | Thames Water Utilities Limited | Rye Meads
11/00055 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Land North of Gilden Way (SRA in Adopted Plan : Planning Permission on Appeal November 2012) | Planning permission granted |  |  | Residential | 911 |  |  | #N/A |  | 17/18: 0; 18/19: 100; 19/20: 200; 20/21: 200; 21/22: 200; 22/23: 211 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.30342 | 0.16653 | 0.30342 | 0.30342 | 0.30342 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.28825 | 0.1582 | 0.28825 | 0.28825 | 0.28825 | 0.0033362 | 0.042176 |  |  | Thames Water Utilities Limited | Rye Meads
17/00097 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Harvey Centre,West Gate, Market Square ,Broad Walk | Planning permission granted |  |  | Residential | 468 |  |  | #N/A |  | 20/21: 100; 21/22: 200; 22/23: 168 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.15587 | 0.033306 | 0.15587 | 0.15587 | 0.15587 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.14808 | 0.031641 | 0.14808 | 0.14808 | 0.14808 | 0.0017139 | 0.021667 |  |  | Thames Water Utilities Limited | Rye Meads
17/00443 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Terminus House (Prior Notification 2016/17) | Planning permission granted |  |  | Residential | 222 |  |  | #N/A |  | 18/19: 100; 19/20: 122 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.073939 | 0.073939 | 0.073939 | 0.073939 | 0.073939 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.070242 | 0.070242 | 0.070242 | 0.070242 | 0.070242 | 0.00081299 | 0.010278 |  |  | Thames Water Utilities Limited | Rye Meads
17/00295 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Former Pearson Education Edinburgh Gate (Prior Notification) | Planning permission granted |  |  | Residential | 250 |  |  | #N/A |  | 17/18: 0; 18/19: 100; 19/20: 150 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.083265 | 0.083265 | 0.083265 | 0.083265 | 0.083265 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.079102 | 0.079102 | 0.079102 | 0.079102 | 0.079102 | 0.00091553 | 0.011574 |  |  | Thames Water Utilities Limited | Rye Meads
14/00361 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Former Rugby Club Ram Gorse (Application Submitted with dwelling increase) | Planning permission granted |  |  | Residential | 125 |  |  | #N/A |  | 18/19: 60; 19/20: 65 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.041633 | 0.041633 | 0.041633 | 0.041633 | 0.041633 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.039551 | 0.039551 | 0.039551 | 0.039551 | 0.039551 | 0.00045776 | 0.005787 |  |  | Thames Water Utilities Limited | Rye Meads
15/00229 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | The Briars,Copshall Close,Ayletts Field(Priority Estate Area) | Planning permission granted |  |  | Residential | 125 |  |  | #N/A | 3 | 18/19: 122 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.041633 | 0.041633 | 0.041633 | 0.041633 | 0.041633 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.039551 | 0.039551 | 0.039551 | 0.039551 | 0.039551 | 0.00045776 | 0.005787 |  |  | Thames Water Utilities Limited | Rye Meads
16/00400 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Motorsales Fifth Avenue | Planning permission granted |  |  | Residential | 142 |  |  | #N/A |  | 19/20: 50; 20/21: 50; 21/22: 42 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.047295 | 0.033306 | 0.047295 | 0.047295 | 0.047295 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.04493 | 0.031641 | 0.04493 | 0.04493 | 0.04493 | 0.00052002 | 0.0065741 |  |  | Thames Water Utilities Limited | Rye Meads
16/00447 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Site at Greenway House, The Parkway, Harlow CM19 5QD PRIOR NOTIFICATION | Planning permission granted |  |  | Residential | 85 |  |  | #N/A |  | 18/19: 85 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.02831 | 0.02831 | 0.02831 | 0.02831 | 0.02831 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.026895 | 0.026895 | 0.026895 | 0.026895 | 0.026895 | 0.00031128 | 0.0039352 |  |  | Thames Water Utilities Limited | Rye Meads
15/00193 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | The Angle | Planning permission granted |  |  | Residential | 69 |  |  | #N/A |  | 19/20: 33; 20/21: 36 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.022981 | 0.022981 | 0.022981 | 0.022981 | 0.022981 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.021832 | 0.021832 | 0.021832 | 0.021832 | 0.021832 | 0.00025269 | 0.0031944 |  |  | Thames Water Utilities Limited | Rye Meads
17/00482 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Mitre Buildings Kitson Way (PD PrNotice) | Planning permission granted |  |  | Residential | 66 |  |  | #N/A |  | 19/20: 66 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.021982 | 0.021982 | 0.021982 | 0.021982 | 0.021982 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.020883 | 0.020883 | 0.020883 | 0.020883 | 0.020883 | 0.0002417 | 0.0030556 |  |  | Thames Water Utilities Limited | Rye Meads
16/00381 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Astra House (Prior Notification) | Planning permission granted |  |  | Residential | 50 |  |  | #N/A |  | 18/19: 50 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.016653 | 0.016653 | 0.016653 | 0.016653 | 0.016653 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.01582 | 0.01582 | 0.01582 | 0.01582 | 0.01582 | 0.00018311 | 0.0023148 |  |  | Thames Water Utilities Limited | Rye Meads
16/00126 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | 1st, 2nd, 3rd Market House (Prior Notification) plus new floor | Planning permission granted |  |  | Residential | 46 |  |  | #N/A |  | 19/20: 46 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.015321 | 0.015321 | 0.015321 | 0.015321 | 0.015321 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.014555 | 0.014555 | 0.014555 | 0.014555 | 0.014555 | 0.00016846 | 0.0021296 |  |  | Thames Water Utilities Limited | Rye Meads
17/00187 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Westgate House West Square (PD PrNotice) | Planning permission granted |  |  | Residential | 40 |  |  | #N/A |  | 19/20: 40 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.013322 | 0.013322 | 0.013322 | 0.013322 | 0.013322 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.012656 | 0.012656 | 0.012656 | 0.012656 | 0.012656 | 0.00014648 | 0.0018519 |  |  | Thames Water Utilities Limited | Rye Meads
17/00183 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Shield House Elizabeth Way (PD PrNotice) | Planning permission granted |  |  | Residential | 35 |  |  | #N/A |  | 19/20: 35 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.011657 | 0.011657 | 0.011657 | 0.011657 | 0.011657 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.011074 | 0.011074 | 0.011074 | 0.011074 | 0.011074 | 0.00012817 | 0.0016204 |  |  | Thames Water Utilities Limited | Rye Meads
15/00504 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Churchgate Hotel | Planning permission granted |  |  | Residential | 26 |  |  | #N/A |  | 18/19: 26 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0086596 | 0.0086596 | 0.0086596 | 0.0086596 | 0.0086596 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0082266 | 0.0082266 | 0.0082266 | 0.0082266 | 0.0082266 | 9.5215e-05 | 0.0012037 |  |  | Thames Water Utilities Limited | Rye Meads
14/00125 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Peartree Business Centre South Rd. CM20 2BD (PD PrNotice) PRIOR NOTIFICATION | Planning permission granted |  |  | Residential | 24 |  |  | #N/A |  | 19/20: 24 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0079934 | 0.0079934 | 0.0079934 | 0.0079934 | 0.0079934 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0075938 | 0.0075938 | 0.0075938 | 0.0075938 | 0.0075938 | 8.7891e-05 | 0.0011111 |  |  | Thames Water Utilities Limited | Rye Meads
16/00446 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Gemini Hse. Flex Meadow CM19 5TJ PRIOR NOTIFICATION | Planning permission granted |  |  | Residential | 22 |  |  | #N/A |  | 18/19: 22 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0073273 | 0.0073273 | 0.0073273 | 0.0073273 | 0.0073273 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.006961 | 0.006961 | 0.006961 | 0.006961 | 0.006961 | 8.0567e-05 | 0.0010185 |  |  | Thames Water Utilities Limited | Rye Meads
13/00084 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | 1 & 1a Walfords Close | Planning permission granted |  |  | Residential | 12 |  |  | #N/A |  | 19/20: 12 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0039967 | 0.0039967 | 0.0039967 | 0.0039967 | 0.0039967 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0037969 | 0.0037969 | 0.0037969 | 0.0037969 | 0.0037969 | 4.3945e-05 | 0.00055556 |  |  | Thames Water Utilities Limited | Rye Meads
17/00118 |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Redevelopment Of Land Rear Of 28-32 Mulberry Green | Planning permission granted |  |  | Residential | 12 |  |  | #N/A |  | 20/21: 12 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.0039967 | 0.0039967 | 0.0039967 | 0.0039967 | 0.0039967 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.0037969 | 0.0037969 | 0.0037969 | 0.0037969 | 0.0037969 | 4.3945e-05 | 0.00055556 |  |  | Thames Water Utilities Limited | Rye Meads
Small Sites 9 dwellings and below |  | No GIS | Harlow District Council | Yes | Housing | Harlow | Small Sites 9 dwellings and below | Planning permission granted |  |  | Residential | 85 |  |  | #N/A |  | 18/19: 17; 19/20: 17; 20/21: 17; 21/22: 17; 22/23: 17 | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.02831 | 0.016986 | 0.02831 | 0.02831 | 0.02831 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.026895 | 0.016137 | 0.026895 | 0.026895 | 0.026895 | 0.00031128 | 0.0039352 |  |  | Thames Water Utilities Limited | Rye Meads
Harlow Completions |  | No GIS | Harlow District Council | Yes |  |  |  | Completed |  |  | Residential | 727 |  |  | #N/A | 727 | [18 empty] | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.24213 | 0.24213 | 0.24213 | 0.24213 | 0.24213 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.23003 | 0.23003 | 0.23003 | 0.23003 | 0.23003 | 0.0026624 | 0.033657 |  |  | Thames Water Utilities Limited | Rye Meads
East Hertfordshire District |  | No GIS | East Hertfordshire District Council | No | Housing |  |  | Emerging allocation |  |  | Residential | 6434 |  |  | #N/A | 343 | 220 | 428 | 390 | 330 | 300 | 341 | 439 | 405 | 371 | 382 | 409 | 367 | 367 | 367 | 356 | 329 | 290 |  | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 2.1429 | 0.56987 | 1.0645 | 1.6959 | 2.1429 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 2.0358 | 0.54137 | 1.0112 | 1.6111 | 2.0358 | 0.023562 | 0.29787 |  |  | Thames Water Utilities Limited | Rye Meads
North Hertfordshire District |  | No GIS | North Hertfordshire District Council | No | Housing |  |  | Emerging allocation |  |  | Residential | 4803 |  |  | #N/A | 45 | 43 | 83 | 253 | 453 | 596 | 439 | 253 | 211 | 203 | 303 | 403 | 253 | 253 | 253 | 253 | 253 | 253 |  | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 1.5997 | 0.29209 | 0.79135 | 1.2626 | 1.5997 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 1.5197 | 0.27749 | 0.75178 | 1.1995 | 1.5197 | 0.017589 | 0.22236 |  |  | Thames Water Utilities Limited | Rye Meads
Stevenage District |  | No GIS | Stevenage District Council | No | Housing |  |  | Emerging allocation |  |  | Residential | 7049 |  |  | #N/A | 145 | 369 | 293 | 373 | 476 | 847 | 798 | 723 | 645 | 520 | 370 | 320 | 320 | 320 | 320 | 170 | 20 | 20 |  | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 2.3477 | 0.55155 | 1.5551 | 2.1712 | 2.3477 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 2.2304 | 0.52397 | 1.4773 | 2.0627 | 2.2304 | 0.025814 | 0.32634 |  |  | Thames Water Utilities Limited | Rye Meads
Welwyn Hatfield District |  | No GIS | Welwyn Hatfield District | No | Housing |  |  | Emerging allocation |  |  | Residential | 6479 |  |  | #N/A | 283 | 322 | 359 | 436 | 445 | 585 | 676 | 659 | 569 | 473 | 374 | 355 | 80 | 260 | 236 | 196 | 91 | 80 |  | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 2.1579 | 0.6145 | 1.4435 | 1.9571 | 2.1579 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 2.05 | 0.58377 | 1.3713 | 1.8592 | 2.05 | 0.023727 | 0.29995 |  |  | Thames Water Utilities Limited | Rye Meads
Epping Forest District |  | No GIS | Epping Forest District Council | No | Housing |  |  | Emerging allocation |  |  | Residential | 605 |  |  | #N/A | 1 | 5 | 12 | 26 | 53 | 59 | 45 | 52 | 52 | 52 | 52 | 44 | 34 | 14 | 1 | 41 | 41 | 21 |  | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.2015 | 0.032307 | 0.10158 | 0.16686 | 0.2015 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.19143 | 0.030691 | 0.096504 | 0.15852 | 0.19143 | 0.0022156 | 0.028009 |  |  | Thames Water Utilities Limited | Rye Meads
Broxbourne District |  | No GIS | Broxbourne District Council | No | Housing |  |  | Emerging allocation |  |  | Residential | 1298 |  |  | #N/A | 5 | 58 | 135 | 266 | 237 | 278 | 134 | 10 | 8 | 103 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 0.43231 | 0.23348 | 0.37669 | 0.42165 | 0.43231 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 0.4107 | 0.2218 | 0.35786 | 0.40057 | 0.4107 | 0.0047534 | 0.060093 |  |  | Thames Water Utilities Limited | Rye Meads
Neighbouring Authority Employment |  | No GIS | East Hertfordshire District Council | No | Employment |  |  | Emerging allocation |  |  | Employment | 0 | 235235 | Mixed B | 23524 | 527 | 801 | 1265 | 1975 | 2128 | 2574 | 2058 | 1674 | 1551 | 1588 | 1283 | 1292 | 960 | 1017 | 833 | 821 | 656 | 521 |  | 0 | Affinity Water | WRZ5 | 0.122 | 2.73 | 0.1 | 2.3524 | 0.6696 | 1.4553 | 2.0693 | 2.3524 |  |  |  |  | Thames Water Utilities Limited | Rye Meads | 95% | 2.2348 | 0.63612 | 1.3825 | 1.9658 | 2.2348 | 0.025866 | 0
43095
[12 empty] | 8739 | In Harlow
[12 empty] | 15700 | In Harlow-Gilston
Note on S7: Anna Beasley: Trajectory source information: Harlow commitments and allocations: DRAFT-ALLOCATION BASED DWELLING TRAJECTORY 2011-2033 V1 Based on completions 2017-18 Received from Colin Endean on 06/03/2018 Harlow Giston New Town sites: Draft Housing Delivery Trajectory - Harlow-Gilston Email from Sarah Pullin to Vicky Forgione 12/01/2018
Note on P8: Anna Beasley: Assumed employment space will be 50% of land area, allowing for access, car parks, landscaping etc.
Note on BI8: Paul Eccleston: Used for flood risk assessment
Note on BJ8: Paul Eccleston: An instantaneous peak flow for assessment of local sewerage capacity
Note on BM8: Paul Eccleston: Usually the same as the company treating the wastewater, but in some cases may be another provider
Note on R31: Anna Beasley: Employment sites -Trajectory spread evenly across 20/21 to 30/31
Note on O34: Anna Beasley: Total number is 10,000. Trajectory states 3000 2030-40, 3000 2040-50, 1850 2050+)
Note on O35: Anna Beasley: No info on trajetcory, placed in 21/22
Note on A39: Anna Beasley: Hospital site location as yet unconfirmed
Note on J43: Anna Beasley: Awaiting S106

## WwTW
ALL GROWTH | Overview |  | Permit (current) | [7 empty] | Housing growth over plan period (dwellings) |  |  | Employment growth over plan period (m2) |  |  | Headroom Assessment | [14 empty] | RAG Assessment
[17 empty] | Present day (2017) |  | End of AMP6 (2020) |  |  | End of AMP7 (2025) |  |  | End of AMP8 (2030) |  |  | End of AMP9 (2035)
| WwTW | Operator | Permit reference | Permitted Maximum DWF (Ml/d) | Permitted Maximum DWF (m3/d) | BOD 95%ile (mg/l) | NH4 95%ile (mg/l) | P Annual Mean (Mg/l) | Recent changes to permit | Proposed changes to permit | Within Study Area | Within neighbouring LPAs | Total | Within Study Area | Within neighbouring LPAs | Total | Observed 80%ile DWF (Ml/d) | Headroom % of Permitted | Additional DWF (Ml/d) | Total DWF (Ml/d) | Headroom % of Permitted | Additional DWF (Ml/d) | Total DWF (Ml/d) | Headroom % of Permitted | Additional DWF (Ml/d) | Total DWF (Ml/d) | Headroom % of Permitted | Additional DWF (Ml/d) | % Difference of Additional DWF | Total DWF (Ml/d) | Headroom % of Permitted | WwTW Flow Capacity RAG | WwTW Flow Capacity Comments
| Rye Meads | TWUL | CLCR.0048 | 110 | 110000 | 10 | 5 | Not conditioned | TBC | TBC | 15700 | 27357 | 43057 | 135000 | 235235 | 370235 | 79.83 | 27.43% | 4.23 | 84.06 | 23.58% | 10.21 | 90.04 | 18.15% | 15.691 | 95.521 | 13.16% | 18.393 | 23.0402 | 98.223 | 10.71%
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
[13 empty] | 0 |  |  | 0 |  | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | 0 | #DIV/0!
Note on M6: Anna Beasley: Total for Harlow District and Harlow-Gilston GT
Note on N6: Anna Beasley: Calculated from number within Rye Meads catchment provided by Chris Colloff
Note on Q6: Anna Beasley: Estimated based on same ratio to residential

## Lookups
This table records lookup values used elsewhere in this spreadsheet. CHANGE THESE VALUES WITH CAUTION!!
Site use | Status | RAG | RYAG | WwTW
Greenfield | Unknown | Not assessed | Not assessed | Unknown
Residential | Completed | Red | Red | No existing public sewerage
Employment | Planning permission granted | Amber | Yellow | Rye Meads
Mixed | Allocated | Green | Amber
Unknown | Emerging allocation |  | Green
Brownfield | Rejected
Emerging

## Water Companies
This table records the water companies in the WCS area, and their per capita consumption for metered housing
Water Supply Company | Abbreviation | Per capita domestic consumption (m3/person/day) | Average occupancy (persons per household) | Per capita employment consumption (m3/person/day) | Link to data source | Comments
Affinity Water | AfW | 0.122 | 2.73 | 0.1 | ..\..\Data Management\Incoming Data\Third Party\Affinity\WRMP\FINAL-WRMP-Jun-2014.pdf | Source - Affinity Water WRMP (2014) PCC for new metered properties Zone 6 population (526,614) divided by number of properties (192,458) = 2.73 persons per household
Anglian Water | AWSL | 0.133 | 2.3 | 0.1
Note on E3: Paul Eccleston: In the absence of information about the type of employment use, the default position would be to use the 0.1m3/day for offices/factories with a canteen as defined in British Water Flows and Loads 4.

## Wastewater Company
This table records the sewerage in the WCS area, and the average occupancy and percentage return to sewer for wastewater flow calculations
Wastewater company / sewerage undertaker | Abbreviation | Average occupancy (persons per household) | Percentage of water used returned to sewer | Per capita employment consumption (m3/person/day) | Link to data source | Comments
Thames Water Utilities Limited | TWUL | 2.4 | 95% | 0.1 |  | Advised by Thames Water
Note on E3: Paul Eccleston: In the absence of information about the type of employment use, the default position would be to use the 0.1m3/day for offices/factories with a canteen as defined in British Water Flows and Loads 4.

## Employment land
This table is used to define emplyment density (m2 per employee) by use class.
Source: | Homes & Communities Agency (2015) Employment Density Guide 3rd Edition.
Web: | https://www.gov.uk/government/uploads/system/uploads/attachment_data/file/484133/employment_density_guide_3rd_edition.pdf
Assumptions:
Where a range of densities is given, the highest density is assumed for WCS planning purposes
Use class | Description | Density (m2/employee)
B1a | Offices | 8
B1b | R&D space | 40
B1c | Light industrial | 47
B2 | Industrial and manufacturing | 36
B8 | Storage and distribution | 70
Mixed B | Mixed | 10
B8 Sui Generis | Data centres | 180
A1 | Retail | 15
A2 | Finance and professional services | 16
A3 | Restaurants and cafes | 15
C1 | Hotels | requires bed count
D2 | Leisure | 65
This table records lookup values used elsewhere in this spreadsheet. CHANGE THESE VALUES WITH CAUTION!!

## Greenfield Runoff Rates
Site Location | GIS ID | Site Area (Ha) | River catchment | Catchment Greenfield Runoff Rate 1 in 2-year (l/s/ha) | Site Greenfield Runoff Rate 1 in 2-year (l/s) | Catchment Greenfield Runoff Rate 1 in 30-year (l/s/ha) | Site Greenfield Runoff Rate 1 in 30-year (l/s) | Catchment Greenfield Runoff Rate 1 in 100-year (l/s/ha) | Site Greenfield Runoff Rate 1 in 100-year (l/s)
Harlow Business Park, The Pinnacles | ED1-01 | 4.7016 | Canons Brook | 1.7 | 7.9927 | 3.9 | 18.3362 | 5.2 | 24.4483
Princess Alexandra Hospital | HS2-1 | 14.0057 | Canons Brook | 1.7 | 23.8096 | 3.9 | 54.6221 | 5.2 | 72.8295
Pollard Hatch plus garages and adjacent land | HS2-10 | 0.33389 | Canons Brook | 1.7 | 0.56761 | 3.9 | 1.3022 | 5.2 | 1.7362
Land between Second Avenue and St. Andrews Meadow | HS2-11 | 0.40988 | Canons Brook | 1.7 | 0.6968 | 3.9 | 1.5985 | 5.2 | 2.1314
Coppice Hatch and garages | HS2-12 | 0.33535 | Canons Brook | 1.7 | 0.5701 | 3.9 | 1.3079 | 5.2 | 1.7438
Sherards House | HS2-13 | 0.48028 | Canons Brook | 1.7 | 0.81647 | 3.9 | 1.8731 | 5.2 | 2.4974
Elm Hatch and public house | HS2-14 | 0.20064 | Canons Brook | 1.7 | 0.34109 | 3.9 | 0.78249 | 5.2 | 1.0433
Fishers Hatch | HS2-16 | 0.19182 | Canons Brook | 1.7 | 0.32609 | 3.9 | 0.74808 | 5.2 | 0.99744
Slacksbury Hatch and associated garages | HS2-17 | 0.23642 | Canons Brook | 1.7 | 0.40191 | 3.9 | 0.92203 | 5.2 | 1.2294
Garage blocks adjacent to Nicholls Tower | HS2-18 | 0.34176 | Canons Brook | 1.7 | 0.58099 | 3.9 | 1.3329 | 5.2 | 1.7771
Stewards Farm | HS2-19 | 0.49561 | Canons Brook | 1.7 | 0.84253 | 3.9 | 1.9329 | 5.2 | 2.5771
Land between Barn Mead and Five Acres | HS2-20 | 0.32094 | Canons Brook | 1.7 | 0.5456 | 3.9 | 1.2517 | 5.2 | 1.6689
Pypers Hatch | HS2-21 | 0.20159 | Canons Brook | 1.7 | 0.3427 | 3.9 | 0.7862 | 5.2 | 1.0483
Land east of Katherines Way, west of Deer Park | HS2-3 | 2.3603 | Canons Brook | 1.7 | 4.0125 | 3.9 | 9.2052 | 5.2 | 12.2736
Lister House, Staple Tye Mews, Staple Tye Depot and The Gateway Nursery | HS2-4 | 0.96217 | Canons Brook | 1.7 | 1.6357 | 3.9 | 3.7525 | 5.2 | 5.0033
South of Clifton Hatch | HS2-5 | 0.77159 | Canons Brook | 1.7 | 1.3117 | 3.9 | 3.0092 | 5.2 | 4.0123
Riddings Lane | HS2-6 | 1.5463 | Canons Brook | 1.7 | 2.6286 | 3.9 | 6.0304 | 5.2 | 8.0405
Kingsmoor Recreation Centre | HS2-7 | 0.81819 | Canons Brook | 1.7 | 1.3909 | 3.9 | 3.1909 | 5.2 | 4.2546
The Evangelical Lutheran Church, Tawneys Road | HS2-8 | 0.17599 | Canons Brook | 1.7 | 0.29917 | 3.9 | 0.68634 | 5.2 | 0.91512
Land east of 144-154 Fennells | HS2-9 | 0.81528 | Canons Brook | 1.7 | 1.386 | 3.9 | 3.1796 | 5.2 | 4.2395
Avenue Home, Latton Common, Near Harlow, CM17 9NJ | RUR.R1 | 0.38136 | Canons Brook | 1.7 | 0.64831 | 3.9 | 1.4873 | 5.2 | 1.9831
Latton Priory - Land to east of Rye Hill Road, London Road, Harlow, Essex, CM18 7HT | SP 5.1 | 117.0406 | Canons Brook | 1.7 | 198.969 | 3.9 | 456.4583 | 5.2 | 608.611
West of Harlow - Water Lane Area | SP 5.2 | 128.2432 | Canons Brook | 1.7 | 218.0134 | 3.9 | 500.1484 | 5.2 | 666.8645
Gilston Allocation | GA1 | 635.878 | Golden Brook | 1.4 | 890.2292 | 3.3 | 2098.3973 | 4. 4 | 2797.872
London Road | ED1-02 | 15.7124 | Harlowbury Brook | 1.1 | 17.2836 | 2.5 | 39.281 | 3.3 | 51.8509
East Road, Templefields | ED1-03 | 2.2272 | Harlowbury Brook | 1.1 | 2.4499 | 2.5 | 5.568 | 3.3 | 7.3497
Playground west of 93 – 100 Jocelyns | HS2-15 | 0.39335 | Harlowbury Brook | 1.1 | 0.43269 | 2.5 | 0.98338 | 3.3 | 1.2981
The Stow Service Bays | HS2-2 | 0.50478 | Harlowbury Brook | 1.1 | 0.55525 | 2.5 | 1.2619 | 3.3 | 1.6658
Strategic Housing Site East of Harlow | HS3 | 109.103 | Harlowbury Brook | 1.1 | 120.0133 | 2.5 | 272.7574 | 3.3 | 360.0398
East of Harlow - Land East of Harlow, North of Church Langley and South of Sheering Road, Harlow, Essex, CM17 0NG | SP 5.3 | 102.3675 | Pincey Brook | 1.2 | 122.8411 | 2.6 | 266.1556 | 3.2 | 327.5761
Gilston (part of) | Hospital Relocation A | 14 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
East of Harlow (part of) | Hospital Relocation B | 14 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Newhall Phase 2 & 3 (750 + 1550 includes 300 Hubbards Hall Land) | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Land North of Gilden Way (SRA in Adopted Plan : Planning Permission on Appeal November 2012) | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Harvey Centre,West Gate, Market Square ,Broad Walk | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Terminus House (Prior Notification 2016/17) | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Former Pearson Education Edinburgh Gate (Prior Notification) | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Former Rugby Club Ram Gorse (Application Submitted with dwelling increase) | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
The Briars,Copshall Close,Ayletts Field(Priority Estate Area) | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Motorsales Fifth Avenue | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Site at Greenway House, The Parkway, Harlow CM19 5QD PRIOR NOTIFICATION | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
The Angle | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Mitre Buildings Kitson Way (PD PrNotice) | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Astra House (Prior Notification) | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1st, 2nd, 3rd Market House (Prior Notification) plus new floor | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Westgate House West Square (PD PrNotice) | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Shield House Elizabeth Way (PD PrNotice) | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Churchgate Hotel | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Peartree Business Centre South Rd. CM20 2BD (PD PrNotice) PRIOR NOTIFICATION | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Gemini Hse. Flex Meadow CM19 5TJ PRIOR NOTIFICATION | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1 & 1a Walfords Close | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Redevelopment Of Land Rear Of 28-32 Mulberry Green | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Small Sites 9 dwellings and below | No GIS |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Note on A37: Anna Beasley: Awaiting S106

## Change Log
This workbook is designed to manage the majority of site related data in a Water Cycle Study.
CHANGE RECORD
Version | Date | Name | Change | File Name | Assumptions
1 | 2018-03-07 | AB | Template populated with sites | 2017s7149 Harlow WCS Site Tracker v1.0
1.1 | 2018-04-03 | TWUL | TW assessment of sites | 2017s7149 Harlow WCS Site Tracker v1.1_TW
1.2 | 2018-04-04 | RP | Growth from neighbouring authorities added Harlow completions added Employment from neighbouring authorities estimated Fixed trajectory calculation Transferred Ww demand to WwTW tab | 2017s7149 Harlow WCS Site Tracker v1.2
1.4 | 2018-04-12 | FH | Tab added for Greenfield Runoff rates | 2017s7149 Harlow WCS Site Tracker v1.4
2 |  | FH | Draft report version sent to stakeholders | 2017s7149 Harlow WCS Site Tracker v2.0
3 | 2018-05-31 | FH | Draft final report version sent to Harlow Council | 2017s7149 Harlow WCS Site Tracker v3.0
3.1 | 2018-06-25 | FH | RAG assessments carried out by JBA updated. Clarfication of which assessments/comments are by Thames Water and JBA. | 2017s7149 Harlow WCS Site Tracker v3.1

## Template History
This sheet records changes made to the template (do not use this to record site data or assessment being added)
Date | Name | Change | Template File Name
2017-03-08 | PE | Template created | Water Cycle Study Site Tracker TEMPLATE v1
2017-03-23 | PE | WwTW table created